## Sheet1
PROJECT TASK LIST
Project Name:
Task Order/ Contract #:
Date:
LOCATION |  | TOPIC |  | USER GUIDE
To the left is a list of project task topics.
Row # |  |  |  | Below is a checklist providing project tasks.
| 60 | ADMINISTRATIVE |  | Use the below instructions to navigate to desired topics.
Row # |  |  |  | Next to project tasks, use the first column of check boxes to indicate "Required" tasks.
| 76 | FACILITY WIDE DESIGN CONSIDERATIONS |  | As you work through project tasks, use the second column of check boxes to indicate "Completed" tasks.
Row #
| 95 | INFLUENT PUMPING
Row # |  |  |  | INSTRUCTIONS
| 129 | SCREENING |  | In order to see cheklist items corresponding to green topics:
Row # |  |  |  | 1. Check the row # on the left for desired topic.
| 154 | GRIT |  | 2. Ctrl + g
Row # |  |  |  | 3. In the pop-up box, under "Reference", type F# (# being the row you looked up).
| 178 | PRIMARY CLARIFIERS |  | 4. Click "OK"
Row #
| 207 | AERATION BLOWERS
Row #
| 230 | RAS/WAS PUMPING
Row #
| 246 | AERATION BASINS
Row #
| 264 | BIOLOGICAL NUTRIENT REMOVAL
Row #
| 278 | SECONDARY CLARIFIERS
Row #
| 292 | FILTRATION
Row #
| 306 | DISINFECTION: UV Disinfection
Row #
| 320 | DISINFECTION: Hypochlorite Systems
Row #
| 328 | DISINFECTION: Gaseous Chlorine
Row #
| 330 | HIGH RATE TREATMENT
Row #
| 342 | EFFLUENT PUMPING
Row #
| 370 | SLUDGE HANDLING
Row #
| 391 | YARD: GENERAL
Row #
| 410 | YARD: PAVING, GRADING, DRAINAGE, & SITE
Row #
| 428 | ELECTRICAL
Row #
| 449 | INSTRUMENTATION & CONTROLS
Row #
| 459 | BUILDINGS
Row #
| 486 | CUSTOM
|  |  |  | ADMINISTRATIVE | REQUIRED | COMPLETED
|  |  | AD-1 | Have required effluent limits been clearly established?
|  |  | AD-2 | Is there agreement concerning influent loads and flows?
|  |  | AD-3 | Is there agreement concerning the general treatment process flow sheet to be used?
|  |  | AD-4 | Have detailed process calculations been completed and reviewed?
|  |  | AD-5 | Has a detailed hydraulic profile been prepared and included in plans?
|  |  | AD-6 | Have process and process control narratives been completed?
|  |  | AD-7 | Has a detail review meeting of I&C control occurred, which includes treatment staff, process engineer, and I&C engineer?
|  |  | AD-8 | Have NPDES compliance sampling locations been identified?
|  |  | AD-9 | Has the sludge disposal plan been prepared?
|  |  | AD-10 | Has a staffing plan been prepared?
|  |  | AD-11 | Have estimates of power and chemical use, and cost thereof, been established?
|  |  | AD-12 | Is a security plan required? Has one been prepared?
|  |  | AD-13 | Has a LEED (or other green standard) criteria been set for the site or project?
|  |  | AD-14 | Has an Opinion of Probable Construction Cost been prepared?
|  |  | AD-15 | Has a sequence of construction necessary to protect continued operations been developed, reviewed and agreed upon?
FACILITY WIDE DESIGN CONSIDERATIONS
|  |  | FWD-1 | Have preliminary PID's been prepared? (@30% review)
|  |  | FWD-2 | Have final PID's been prepared? (@90% review)
|  |  | FWD-3 | Have influent and NPDES compliance monitoring stations been established? Are auto samplers provided?
|  |  | FWD-4 | Have seal water systems been provided for all pumps, blowers or compressors requiring seal water?
|  |  | FWD-5 | Do all seal water systems have backflow previention?
|  |  | FWD-6 | Is no flow signal from seal water a shutdown and "Do Not Start" condition for the serviced equipment?
|  |  | FWD-7 | Have all potable water system connections to plant, process or non-potable systems been provided with gap tanks?
|  |  | FWD-8 | Do all plant, process or non-potable water systems entering sewage wet wells have backflow protection?
|  |  | FWD-9 | Has each flow meter been checked to determine if piping configuration has created a piping high point requiring air release?
|  |  | FWD-10 | Are piping air release points limited to manual release on raw sewage and sludge lines and either automatic or manual release on non-solids laden water lines?
|  |  | FWD-11 | Are required site security features included in the design?
|  |  | FWD-12 | Has a standby power plan been prepared?
|  |  | FWD-13 | Are all chemical storage and feed systems in secondary containment?
|  |  | FWD-14 | Have eye washes and safety showers been provided adjacent to all chemical storage and feed systems?
|  |  | FWD-15 | Has there been a safety analysis/audit performed? This may include adequate handrails, cages on ladders, safety signage, smoke/fire alarms, emergency exit signs, emergency egress lighting, etc.
|  |  | FWD-16 | Has confined space and floor slab load rating signage been provided?
|  |  | FWD-17 | Have all hazard rated areas been identified and are the class and division ratings shown on the plans?
|  |  | FWD-18 | Have all motors and equipment been checked for appropriate NEMA rating in hazard rated areas?
INFLUENT PUMPING
|  |  | IN-1 | If pumps are VFD controlled, has range of operation been defined in relation to system head curve?
|  |  | IN-2 | Is peak flow firm capacity provided?
|  |  | IN-3 | Is NPSH required provided at lowest planned wet well operating level?
|  |  | IN-4 | Are pumps within acceptable range on their operating curve at all wet well levels and all VFD speed setting?
|  |  | IN-5 | Have pumps been checked for short cycling when flow = 1/2 pump capacity? At full range of planned VFD settings?
|  |  | IN-6 | Are pump motors non-overloading across entore pump curve?
|  |  | IN-7 | Do pumps auto restart on transfer to standby power?
|  |  | IN-8 | Is there a split wetwell? Can half of the station be removed from service for maintenance?
|  |  | IN-9 | Can pumps, motors, valves, gates in enclosed areas be removed?
|  |  | IN-10 | Is there adequate work space (x-ft minimum clear) around equipment needing maintenance?
|  |  | IN-11 | Are pump on/off sequence and other control schemes defined?
|  |  | IN-12 | Are electrical and control equipment out of hazard rated areas or in rated enclosures?
|  |  | IN-13 | Are electrical and control equipment above the static high water elevation?
|  |  | IN-14 | What type of check valve or actuated check valve has been selected?
|  |  | IN-15 | Are valve operators at a working height, provided with chain operators, or have remote operating stations?
|  |  | IN-16 | Are gate and valve operators physically accessible or are they blocked by piping, control boxes, or similar obstructions?
|  |  | IN-17 | If seal water is required, is there a seal water system (including hub or floor drains in the vicinity of each pump equipment pad)?
|  |  | IN-18 | Is there an adequately sized crane for removal of pumps and motors? Is the travel path of the crane with a load clear of obstructions? Is overall crane coverage adequate?
|  |  | IN-19 | Wet/Dry Pit: is there stair access into both sides of station?
|  |  | IN-20 | Wet/Dry Pit: is there ventilation for both sides of station? Is there warning light for loss of ventilation in wetwell?
|  |  | IN-21 | Wet/Dry Pit: is dry well ventilation supplied to bottom of well and is dry well positive to wet well?
|  |  | IN-22 | Wet/dry pit: Are there wash down hose bibs on both sides of station? Does water line (whether potable or non-potable) have a reduced-pressure backflow preventer installed before entering wetwell?
|  |  | IN-23 | Is there a sump pump or drain line in all dry wells, valve vaults, and other below grade dry spaces?
|  |  | IN-24 | Submersible: Is there standing height, lights and, ventilation in all valve vaults?
|  |  | IN-25 | Is there a logical (even if inconvenient) method to remove larger debris from wet well?
|  |  | IN-26 | Submersible: Does wet well meet explosion proof requirement by either using explosion proof rated pumps or having normal all pumps off elevation such that electrical connections remain submerged?
|  |  | IN-27 | Does wetwell level element correctly reflect level seen by pump and is it isolated from turbulence?
|  |  | IN-28 | Are suction lines limited to 5 fps at maximum flow?
|  |  | IN-29 | Are discharge lines limited to 10 fps at maximum flow? With both current and any planned larger pump?
|  |  | IN-30 | Has maximum solids size passing through volute been established?
|  |  | IN-31 | Are increased capacity provisions included, such as installing a larger impeller for the motor size supplied initially, ability to install larger pumps, or space for additional pumps?
|  |  | IN-32 | Does wetwell geometry comply with Hydraulic Institute Standards?
|  |  | IN-33 | Is odor control required? Haas it been provided? Can it easily be added in the future?
SCREENING
|  |  | SC-1 | Has the selected screen opening size been used?
|  |  | SC-2 | On combined sewers or other lines with heavy leaf load has a multiple rake screen been selected?
|  |  | SC-3 | Will screen handle peak hour hydraulic flowrate? (screens rarely have any capacity beyond rated)
|  |  | SC-4 | Is floor opening in front of screen enclosed or fall protected?
|  |  | SC-5 | Are routine lubrication points accessible or have lube lines been extended?
|  |  | SC-6 | Do motors and controls have correct NEMA rating?
|  |  | SC-7 | Can any electrical components, including instruments, be submerged? If yes is it rated for submersible service?
|  |  | SC-8 | Has firm capacity been provided?
|  |  | SC-9 | How is screen activated? (timer, level?)
|  |  | SC-10 | Is there adequate work space around equipment needing maintenance?
|  |  | SC-11 | Does screenings discharge and conveyance prevent spillage?
|  |  | SC-12 | How are screenings dewatered?
|  |  | SC-13 | Will influent flow equally divide between parallel screens or will flow short circuit through one unit?
|  |  | SC-14 | Is there adequate truck access to screenings dumpster?
|  |  | SC-15 | If screenings dumpster is inside building is necessary portion of floor designed for truck wheel loads?
|  |  | SC-16 | Do screenings get delivered to dumpster without operators having to do a transfer function?
|  |  | SC-17 | Do screens and related equipment auto restart on transfer to standby power?
|  |  | SC-18 | Has maximum approach velocity in upstream channel been defined? Has it been provided?
|  |  | SC-19 | Is straight-channel distance ahead of screens adequate?
|  |  | SC-20 | Has maximum through-screen velocity been determined for clean and 50-percent clogged conditions?
|  |  | SC-21 | Are alarm conditions defined?
|  |  | SC-22 | Is odor control necessary in this area? Can it easily be added?
|  |  | SC-23 | Are there sufficient hose bibbs for wash down and convenience electrical outlets for maintenance?
|  |  | SC-24 | For screens after pumping, are there gravity drains on the screen channels between the isolation gate valves?
GRIT
|  |  | GR-1 | What type of grit collection has been selected (vortex, aerated channel, etc)?
|  |  | GR-2 | Has firm peak hour capacity been provided in the grit tank?
|  |  | GR-3 | Has firm peak hour capacity been provided in the grit pumps?
|  |  | GR-4 | Has firm peak hour capacity been provided in the grit classifier?
|  |  | GR-5 | Do grit pumps have a positive flooded suction?
|  |  | GR-6 | Have 45 deg bends and Y's been used instead of 90 deg bends, where possible, in grit conveying piping?
|  |  | GR-7 | Do all grit conveying pipes have the ability to be flushed or otherwise cleaned?
|  |  | GR-8 | Are all grit pipes freeze protected?
|  |  | GR-9 | Does grit pump room have a sump pump?
|  |  | GR-10 | Is there adequate work space around equipment needing maintenance?
|  |  | GR-11 | For aerated grit tanks or vortex hopper scour, have the blowers been provided with sound protection (separate room or enclosure)?
|  |  | GR-12 | Can equipment in enclosed areas be removed?
|  |  | GR-13 | Will influent flow equally divide between parallel grit tanks or will flow short circuit through one unit?
|  |  | GR-14 | Will grit tank(s) work over the full range of plant flows?
|  |  | GR-15 | Is there adequate truck access to grit dumpster?
|  |  | GR-16 | If dumpster is inside building is necessary portion of floor rated for truck wheel load?
|  |  | GR-17 | Do grit collectors, pumps and classifiers auto restart on transfer to standby power?
|  |  | GR-18 | Has maximum approach velocity in upstream channel been defined? Has it been provided?
|  |  | GR-19 | Is straight-channel distance ahead of grit removal tanks adequate?
|  |  | GR-20 | Is the cyclone supply line properly vented?
|  |  | GR-21 | Is the classifier drain free-discharging (non-submerged)?
|  |  | GR-22 | Is the cyclone/classifier located above the water surface or have siphoning provisions been taken (such as installing ball checks)?
|  |  | GR-23 | Is odor control required? Haas it been provided? Can it easily be added in the future?
PRIMARY CLARIFIERS
|  |  | PR-1 | Does historic waste strength records justify the existance fo primaries or should this unit process be eliminated?
|  |  | PR-2 | Is side water depth at least 10 feet (per TSS 72.1)?
|  |  | PR-3 | Is surface overflow rate less than 1,000 gpd/sf at ADDF AND less than 2,000 gpd/sf at peak hour (per TSS 72.2)?
|  |  | PR-4 | On rectangular tanks, what is chain material(steel, plastic, or stainless steel)?
|  |  | PR-5 | Do collectors run continuously or intermittently? If intermittently, what is control scheme and what are components?
|  |  | PR-6 | What controls withdrawal of sludge (T-valve, pump, pump and valve)?
|  |  | PR-7 | Is sludge withdrawal controlled separately for each clarifier?
|  |  | PR-8 | Do primary sludge pumps have a positive flooded suction?
|  |  | PR-9 | Can primary sludge lines be flushed?
|  |  | PR-10 | Is there adequate work space around equipment needing maintenance?
|  |  | PR-11 | Can equipment in enclosed areas be removed?
|  |  | PR-12 | Does sludge pump area have a sump pump?
|  |  | PR-13 | Do the collectors and sludge pumps auto restart on transfer to standby power?
|  |  | PR-14 | Are NPW sprays needed for the main clarifier tank? or are provisions for a future system provided?
|  |  | PR-15 | How is scum removed from clarifiers?
|  |  | PR-16 | Are there NPW sprays on the scum troughs?
|  |  | PR-17 | How is scum handled after it leaves clarifier?
|  |  | PR-18 | How is scum disposed?
|  |  | PR-19 | For circular tanks, is floor slope at least 1" in 12"?
|  |  | PR-20 | Have torque ratings been defined for "minimum running" condition, "alarm" condition (70% of running), "cutout" condition (110% of running), and "ultimate" condition (200% of running)? Are shear pins limiting?
|  |  | PR-21 | For circular tanks, is rotational speed defined?
|  |  | PR-22 | Has minimum walkway clear width, support system, grating type and material, and handrail type and material been defined?
|  |  | PR-23 | Have scum baffles been included, and type of material defined?
|  |  | PR-24 | Have inlet baffles been included, to dampen influent current?
|  |  | PR-25 | CEPT: What coagulant has been selected? What is basis of selection?
|  |  | PR-26 | CEPT: Does it run continuously or only during high flow? If high flow what triggers startup? Is startup automatic?
|  |  | PR-27 | CEPT: How/where is coagulant delivered and stored? What operator activity is required to receive coagulant?
|  |  | PR-28 | CEPT: What is type size, and speed of flocculaor mixer? What is flocculation time at peak? At ADDF?
AERATION BLOWERS
|  |  | AE-1 | Do design calculations include complete headloss calculations including flow meters, flow conditioners, dirty inlet filters, dirty diffusers and all piping?
|  |  | AE-2 | Is there adequate space to change filters in filter/silencer housing?
|  |  | AE-3 | Are pressure gauges on inlet and discharge piping provided? Accessible to read?
|  |  | AE-4 | Is discharge pipe insulated in areas used for access or maintenance?
|  |  | AE-5 | Is there adequate space between the isolation valves and check valves (inlet and discharge installations)?
|  |  | AE-6 | Is there discharge flow measurement, with flow meter installed correctly, and local display accessible to read?
|  |  | AE-7 | Is there noise mitigation, either equipment- or room-specific?
|  |  | AE-8 | Have inlet and discharge velocities ranges been verified to be within typical ranges?
|  |  | AE-9 | Have dirty inlet filter pressure losses been defined?
|  |  | AE-10 | Have dirty aeration diffuser pressure losses been defined?
|  |  | AE-11 | Has design capacity airflow been defined in standard (scfm), inlet (icfm), and actual (acfm) terms?
|  |  | AE-12 | Do the blowers auto restart on transfer to standby power?
|  |  | AE-13 | If required, is blow-off piping adequately sized to minimize sound and is airstream directed away from access or maintenance work areas?
|  |  | AE-14 | Are condensate drain valves and lines located on low spots in the air line?
|  |  | AE-15 | Are air flow meters installed with proper upstream and downstream diameters?
|  |  | AE-16 | Is blower type (single stage, multi-stage, PD) acceptable?
|  |  | AE-17 | Has blower surge protection been provided?
|  |  | AE-18 | Have soft start staarters or VFD's been provided on large blowers?
|  |  | AE-19 | Has energy saving control (inlet guide vanes on centrifugal or VFD on PD) been provided? How are they controlled?
|  |  | AE-20 | Has blower room been adequately ventilated (temp rise limited to 10 deg)?
|  |  | AE-21 | Are VFD's, PLC's, other heat sensitive electrical components been isolated from blower heat?
|  |  | AE-22 | Can air supply be adequately adjusted for needed range of air demands (from min to max flow rates)?
RAS/WAS PUMPING
|  |  | RA-1 | Does firm RAS pumping rate match or exceed influent pumping rate? (TSS 92.41)
|  |  | RA-2 | Has need for high RAS capacities been evaluated in BNR facilities?
|  |  | RA-3 | Does RAS pumping envelope cover start-up to build-out conditions?
|  |  | RA-4 | Does firm WAS pumping range correspond with SRT range?
|  |  | RA-5 | Are RAS ad WAS pumps within the acceptable portion of their operating range over the full range of possible flow rates?
|  |  | RA-6 | Is the RAS/WAS pump station wetwell mixed?
|  |  | RA-7 | Have sludge sample ports been provided? Are they routed to a sample sink?
|  |  | RA-8 | Are there flushing connections of suction and discharge piping?
|  |  | RA-9 | If seal water is required, are there hub or floor drains in vicinity?
|  |  | RA-10 | Are flow meters installed with proper upstream and downstream diameters, and at low spots in the discharge piping?
|  |  | RA-11 | Can pumps, motors, valves, gates in enclosed areas be removed?
|  |  | RA-12 | Is there adequate work space (x-ft minimum clear) around equipment needing maintenance?
|  |  | RA-13 | Are valve operators at a working height, provided with chain operators, or have remote operating stations?
|  |  | RA-14 | Are gate and valve operators physically accessible or are they blocked by piping, control boxes, or similar obstructions?
|  |  | RA-15 | Does the system auto restart on transfer to standby power?
AERATION BASINS
|  |  | ABA-1 | Is the design solids retention time (SRT) defined?
|  |  | ABA-2 | Is the design mixed liquor suspended solids (MLSS) concentration range defined?
|  |  | ABA-3 | Are walkways arranged ideally for air valve, meter, slide/weir gate, and instrumentation accessibility, as well as for sampling.
|  |  | ABA-4 | Do basins have adequate freeboard for typical and upset operation, for both liquid and foam?
|  |  | ABA-5 | Are there provisions for scum and foam removal?
|  |  | ABA-6 | Is influent equally distributed across basin at point(s) of introduction? (first zone of basin for conventional activited sludge)
|  |  | ABA-7 | Does influent piping allow for step feed?
|  |  | ABA-8 | Is there an efficient way to stop flow into each basin?
|  |  | ABA-9 | Are basin drains sized and configured to adequately dewater basin in a reasonable time (x-hours) and handle heavy solids?
|  |  | ABA-10 | Can each basin be drained without effecting the operation of other basins? If individual basins are divided into compartments, is there a drain in each compartment? Can the baffle wall withstand the hydraulic differential?
|  |  | ABA-11 | Does diffuser and header layout allow spacing for diffuser element replacement?
|  |  | ABA-12 | Is tapered aeration created by diffuser spacing or is aeration system designed with DO or ORP controlled zones? If the latter, how many zones?
|  |  | ABA-13 | Is each DO or ORP probe located for optimal process monitoring and accessibility for cleaning and adjustment?
|  |  | ABA-14 | Is basin depth 22 ft or less and if not, have degasification provisions been made?
|  |  | ABA-15 | Is influent flow equally divided between parallel basins? Is this still true if any particular basin is off-line?
|  |  | ABA-16 | If RAS enters the basin separately from influent, is it equally divided between parallel basins? Is this still true if any particular basin is off-line?
|  |  | ABA-17 | Has sufficient basin freeboard been provided for foam, or turbulence, particularly near surface aerators?
BIOLOGICAL NUTRIENT REMOVAL
|  |  | BNR-1 | Has influent to this unit process been tested for volatile fatty acids (or other measure of C:P ratio) to determine it will support phosphorus removal by BNR?
|  |  | BNR-2 | Are mixers located to maximize mixing and minimize vortexing in anaerobic and anoxic basin installations?
|  |  | BNR-3 | Are zone baffles submerged to allow foam and scum passage and properly ported to insure positive flow through the zone?
|  |  | BNR-4 | Are swing zones employed so that anaerobic and anoxic zone volumes can be increased or decreased to optimize nutrient removal and maintain nitrifier populations?
|  |  | BNR-5 | Is the internal nitrogen-rich recycle (NRCY) pump, flow meter, and piping accessible for inspection and maintenance?
|  |  | BNR-6 | Is the effluent weir accessible for cleaning?
|  |  | BNR-7 | Are self-priming pumps located where scum and foam will collect?
|  |  | BNR-8 | Have increased sludge yields been accounted for their impact to transfer pumping, storage, thickening, and dewatering facilities?
|  |  | BNR-9 | Are pumps and mixers equipped with davits that assist in adjusting operating position and removal for inspection and maintenance?
|  |  | BNR-10 | Are NRCY internal recycles adjustable between 2 and 4 times the forward flow?
|  |  | BNR-11 | Has the hydraulic profiles through the aeration basins taken into account both RAS and NRCY recycle flows?
|  |  | BNR-12 | Are influent flows and RAS flows introduced into the first zone?
|  |  | BNR-13 | Is influent and RAS and MLSS and NARCY recycle adaquately mixed?
SECONDARY CLARIFIERS
|  |  | SE-1 | Is peak hour overflow rate <= 1200 gpd/sf; 1000 gpd/sf if single stage nitrification?(TSS Art 72.232)
|  |  | SE-2 | Is peak solids loading limited to 50 lb/day/sf; 35 lb/day/sf for single stage nitrification? (TSS Art 72.232)
|  |  | SE-3 | Is side water depth at least 12 feet? (TSS 72.1)
|  |  | SE-4 | Is weir loading <= 30,000 gpd/lf?(TSS 72.43)
|  |  | SE-5 | For rectangular unit, what is chain material (iron, stainless steel, or plastic)?
|  |  | SE-6 | Has full width scum protection been provided? (width for rectangular tanks or radius for circular tanks).
|  |  | SE-7 | Can sludge draw off rate be controlled independently from the RAS/WAS pumping system?
|  |  | SE-8 | Can sludge draw-off rate from each clarifier be controlled and measured separately from other clarifiers?
|  |  | SE-9 | Are weirs accessible for cleaning?
|  |  | SE-10 | Have provisions been made to reduce weir biomass accumulations (brush cleaning systems or FRP covers)?
|  |  | SE-11 | Has an energy dissipating outlet been considered for the influent stilling well?
|  |  | SE-12 | Does the system auto restart on transfer to standby power?
|  |  | SE-13 | For clarifiers following BNR reactors, have dual or quadruple skimmers been considered?
FILTRATION
|  |  | FI-1 | What technology has been selected? Granular media ( deep bed mono-media, standard dual media, low head ) or disk filters.
|  |  | FI-2 | Has sufficient head been provided through the filter?
|  |  | FI-3 | Has a source and destination for backwash water been provided?
|  |  | FI-4 | What backwash flow rate is required?
|  |  | FI-5 | What impact on other unit processes will the backwash water flow have? Have impacts been minimized? Are the impacts acceptable?
|  |  | FI-6 | Is hydraulic loading limited to 5 gpm/sf at peak or 2.5 gpm/sf at ADDF with one unit in backwash? (TSS 112.31)
|  |  | FI-7 | Are influent solids limited to less than 20 mg/l?
|  |  | FI-8 | Granular: Has Air/water backwash or surface filter sweeps been provided?
|  |  | FI-9 | Granular: Has porous plate underdrain been avoided or has means of cleaning plate from biofouling been provided?
|  |  | FI-10 | Disk or Traveling bridge: Are units under cover?
|  |  | FI-11 | What level of operator input is required for backwash?
|  |  | FI-12 | Are vendor control panels connected to central SCADA?
|  |  | FI-13 | Does the system auto restart on transfer to standby power?
DISINFECTION: UV Disinfection
|  |  | DUV-1 | What is design intensity and transmissivity?
|  |  | DUV-2 | Is firm capacity provided while lamps are being cleaned?
|  |  | DUV-3 | For non-Ohio River plants can flow be diverted during non-disinfection season?
|  |  | DUV-4 | Is there work space for bulb cleaning activity?
|  |  | DUV-5 | Is the needed lift equipment provided to move lamp modules around?
|  |  | DUV-6 | Has sufficient HVAC been provided to off-set ballast heat? (Temperature is normally limited by UV vendor control panel requirements.) What is acceptable temperature limit?
|  |  | DUV-7 | Are UV exposure signage and face shields provided?
|  |  | DUV-8 | Is channel level controls adequate? Are they fail-safe to prevent draining or flooding a channel?
|  |  | DUV-9 | Are all electrical components either submersible or above the watic water surface?
|  |  | DUV-10 | Is the system on standby power?
|  |  | DUV-11 | Does the system auto restart on transfer to standby power?
|  |  | DUV-12 | Does flow divide equally between parallel channels?
|  |  | DUV-13 | Are UV lamps protected from upstream and downstream debris?
DISINFECTION: Hypochlorite Systems
|  |  | DIH-1 | Is storage tank either fiberglass with vinyl ester resin or UHMW cross linked polyolefin? (all other materials will fail.)
|  |  | DIH-2 | Are all components of storage and feed system(control valve or metering pumps) housed within secondary containment?
|  |  | DIH-3 | Does drainage in truck unloading point go to controlled discharge sump?
|  |  | DIH-4 | Are all tanks (bulk and day) in a location that allows for removal and replacement? (expected tank life is 12-15 years)
|  |  | DIH-5 | Are ball valves vented?
|  |  | DIH-6 | Is mixing provided at point of chemical application?
|  |  | DIH-7 | Is chemical piping inside or above grade accessible for inspection and replacement? Is buried pipe to the extent possible not under pavement?
DISINFECTION: Gaseous Chlorine
|  |  | DIG-1 | By policy, a MSD facility should not have a gaseous chlorine system.
HIGH RATE TREATMENT
|  |  | HRT-1 | Is influent arranged to provide a stable flow rate?
|  |  | HRT-2 | Can flow be re-circulated for 2 hydraulic residence times at startup?
|  |  | HRT-3 | Can system startup with remote operator using SCADA? Followed by operator arriving at unit process.
|  |  | HRT-4 | Is material handling for bagged chemicals and ballast sand acceptable?
|  |  | HRT-5 | Is polymer system curbed to contain spills?
|  |  | HRT-6 | Is primary coagulant system in secondary containment?
|  |  | HRT-7 | Is an eye wash and safety shower provided in the chemical storage and feed area?
|  |  | HRT-8 | Can all sludge be removed from system at shut down?
|  |  | HRT-9 | Are water sprays provided to manage foaming at points of turbulence?
|  |  | HRT-10 | Are sample pumps out of points of grit accumulation?
|  |  | HRT-11 | Does the system auto restart on transfer to standby power?
EFFLUENT PUMPING
|  |  | EFF-1 | Is the firm capacity of the effluent pumps at least equal to the sum of the firm capacity of the influent pumps and any onsite storm water directed to the effluent pumps?
|  |  | EFF-2 | Can effluent pumping be avoided during dry weather?
|  |  | EFF-3 | Has a complete system head curve been developed?
|  |  | EFF-4 | Has connection between pump dischage and plant outfall been checked for any hydraulically limiting restriction?
|  |  | EFF-5 | Are effluent pumps on standby power?
|  |  | EFF-6 | Do the effluent pumps auto restart on transfer to standby power?
|  |  | EFF-7 | Are the efluent pumps on soft start starters or VFD's?
|  |  | EFF-8 | If pumps are VFD controlled, has range of operation been defined in relation to system head curve?
|  |  | EFF-9 | Is NPSH required provided at lowest planned wet well operating level?
|  |  | EFF-10 | Are pumps within acceptable range on their operating curve at all wet well levels and all VFD speed setting?
|  |  | EFF-11 | Have pumps been checked for short cycling when flow = 1/2 pump capacity? At full range of planned VFD settings?
|  |  | EFF-12 | Are pump motors non-overloading across entore pump curve?
|  |  | EFF-13 | Is there a split wetwell? Can half of the station be removed from service for maintenance?
|  |  | EFF-14 | Can pumps, motors, valves, gates in enclosed areas be removed?
|  |  | EFF-15 | Is there adequate work space around all equipment requiring maintenance?
|  |  | EFF-16 | Is there lifting equipment to allow for the removal of pumps?
|  |  | EFF-17 | Are pump on/off sequence and other control schemes defined?
|  |  | EFF-18 | Are electrical and control equipment above the static high water elevation and the 100-year flood elevation?
|  |  | EFF-19 | What type of check valve or actuated check valve has been selected?
|  |  | EFF-20 | Are valve actuators at a working height, provided with chain operators or have remote operating stations?
|  |  | EFF-21 | Are gate and valve operators physically accessible or are they blocked by piping, control boxes, or similar obstructions?
|  |  | EFF-22 | Is there a sump pump or drain line in all dry wells, valve vaults, and other below grade dry spaces?
|  |  | EFF-23 | Is there standing height, lights and ventilation in all valve vaults?
|  |  | EFF-24 | Does wetwell level element correctly reflect level seen by pump and is it isolated from turbulence?
|  |  | EFF-25 | Are discharge lines limited to 10 fps at maximum flow? With both current and any planned larger pump?
|  |  | EFF-26 | Are increased capacity provisions included, such as installing a larger impeller for the motor size supplied initially, ability to install larger pumps, or space for additional pumps?
|  |  | EFF-27 | Does wetwell geometry comply with Hydraulic Institute Standards?
SLUDGE HANDLING
|  |  | SL-1 | Are separate facilities to be used for primary and secondary sludges?
|  |  | SL-2 | Is there adequate work space around all equipment requiring maintenance?
|  |  | SL-3 | At Belt filter Presses is there enough side space to pull a roller out of the press?
|  |  | SL-4 | At centrifuge facility is there enough end space to remove bowl and scroll?
|  |  | SL-5 | Is sludge handling equipment connected to standby power?
|  |  | SL-6 | Does sludge handling equipment auto restart on transfer to standby power?
|  |  | SL-7 | Do conveying systems contain spillage?
|  |  | SL-8 | Can conveyors start under load?
|  |  | SL-9 | Do shutdown sequences empty conveyors?
|  |  | SL-10 | Does dewatering equipment shutdown on failure of discharge conveyor?
|  |  | SL-11 | Does feed to dewatering equipment shut down on loss of chemical feed to unit?
|  |  | SL-12 | Does system provide any temporary storage of liquid or dewatered sludge between unit processes?
|  |  | SL-13 | Does space, arrangement and configuration make cleanup of all equipment convenient?
|  |  | SL-14 | Are chemical feed systems convenient in location and configuration to both fill and operation of the chemical feed systems and the dewatering equipment?
|  |  | SL-15 | Are chemical feed systems in secondary confinement?
|  |  | SL-16 | Has an eye wash and safety shower been provided at chemcical storage and feed areas?
|  |  | SL-17 | Are facilities designed to receive sludge from other facilities adequate? Do they handle a sufficient range of solids concentrations?
|  |  | SL-18 | Are facilities designed to load liquid sludge for transport to other facilities adequate?
|  |  | SL-19 | Are floor/area drains at all sludge facilities adequate and routed to a sanitary line?
|  |  | SL-20 | Is odor control provided at sludge handling facilities? If not can it be easily added?
YARD: General
|  |  | YRDG-1 | Can all yard valve and meter pits be drained by a drain or sump pump? Or are all mechanical and electrical devices in pit submersible?
|  |  | YRDG-2 | Do valve and meter pits have ladder access and lighting?
|  |  | YRDG-3 | Do valve and meter pits have mechanical ventilation? If yes is operation continuous or intermittent?
|  |  | YRDG-4 | Can a person stand up in valve and meter pits?
|  |  | YRDG-5 | Do valve and meter pits have a top hatch large enough to remove equipment?
|  |  | YRDG-6 | Has all outdoor and above grade piping has been provided with freeze protection?
|  |  | YRDG-7 | Is potable water fully protected from cross connect by reduced pressure backflow preventers or gap tanks?
|  |  | YRDG-8 | Are potable, non-potable, and plant water systems looped?
|  |  | YRDG-9 | Has warning signage been provided at non-potable and plant water outlets?
|  |  | YRDG-10 | Where and how is influent flow rate measured?
|  |  | YRDG-11 | Do plant internal recycle flows enter before or after the influent flow meter? If after are the recycle flows metered?
|  |  | YRDG-12 | Where and how is final effluent flow metered?
|  |  | YRDG-13 | Do pipes conveying solids laden flows have minimum and maximum velocities between 2 and 10 fps?
|  |  | YRDG-14 | Are potable water lines crossing sanitary lines adequately separated? (10 ft hort., 1.5 ft vert. or encased)
|  |  | YRDG-15 | To the extent possible are yard piping (particularly chemical lines) not under pavement?
|  |  | YRDG-16 | Are yard piping, electrical duct banks, and I&C duct banks correctly and accurately located on record drawings?
|  |  | YRDG-17 | Are adequate yard hydrants and electrical convenience outlets available? This includes area such as tank walkways.
|  |  | YRDG-18 | Is there adequate isolation valving?
YARD: Paving, Grading, Drainage, and Site
|  |  | YPGD-1 | Is area and arrangement of paving acceptable?
|  |  | YPGD-2 | Does paving have necessary minimum turning radius for trucks and/or pull out/backing areas?
|  |  | YPGD-3 | Is mix of gravel, asphalt, and concrete pavement acceptable?
|  |  | YPGD-4 | Is concrete pavement provided in areas heavy trucks park?
|  |  | YPGD-5 | Are walk ways provided to/from all buildings and unit processes?
|  |  | YPGD-6 | Is access to office and control buildings ADA compliant?
|  |  | YPGD-7 | Is site functional at 25 year flood elevation and protected to 100 year flood elevation? (req. of PL 92-500)
|  |  | YPGD-8 | Is site graded away from all buildings?
|  |  | YPGD-9 | Have all locations where storm water might pool been eliminated?
|  |  | YPGD-10 | Does all storm water sheet flow off site or to drain?
|  |  | YPGD-11 | Are storm drains adequately sized and appropriately exit site?
|  |  | YPGD-12 | Are storm inlets in contaminated areas (sludge, grit handling, chemical handling etc) routed to sanitary?
|  |  | YPGD-13 | Are grassed areas mowable?
|  |  | YPGD-14 | Is general site lighting provided?
|  |  | YPGD-15 | Is specific area work lighting provided? Is it switchable?
|  |  | YPGD-16 | Has a LEED (or other green standard) criteria been set for the site or project?
|  |  | YPGD-17 | Is there appropriate handrail/guardrail for worker safety? (OHSA requires protection at any vertical drop greater than 21 inches)
ELECTRICAL
|  |  | EL-1 | For all equipment not listed elsewhere, do power loads auto restart on transfer to standby power?
|  |  | EL-2 | System-wide are equipment restarts on transfer to standby power staggered sufficiently to keep running loads and inrush currents within the capacity of the generoator?
|  |  | EL-3 | Are power saving devices being used?
|  |  | EL-4 | Are all buildings and structures correctly grounded?
|  |  | EL-5 | Do grounding systems have test ports?
|  |  | EL-6 | Are all buildings and structures adequately lightning protected?
|  |  | EL-7 | What type conduit is being used inside buildings? PVC? RMC? Aluminum? PVC coated RMC?
|  |  | EL-8 | Are all buried conduit in concrete ductbanks?
|  |  | EL-9 | Have all panels, lights, and other electrical devices been checked for appropriate NEMA rating in hazard rated areas?
|  |  | EL-10 | Is space over MCC's free of piping, drains and any other fluid carrying devices?
|  |  | EL-11 | Is there at lease 4'-0" clear in front of all MCC's, and panels?
|  |  | EL-12 | Are all MCC's, PLC's and other significant electrical items above static water level?
|  |  | EL-13 | Do VFD's have cabinet coolers or are located where temperature will not exceed 90 deg F
|  |  | EL-14 | Are MCC's of dual feed double end design? If yes, has a manual tie-break switch been provided?
|  |  | EL-15 | Are MCC rooms postively pressurized relative to adjacent process areas?
|  |  | EL-16 | Has the heat load from all electrical equipment in each MCC room been accounted in the heat load calculation for HVAC in the space? This is particularly important for VFD's, transformers and other high heat load devices. Only installed spare equipment that can not run at peak conditions may be excluded.
|  |  | EL-17 | Do feeders to MCC have extra capacity for future expansion?
|  |  | EL-18 | Have sufficient spare or open space MCC cubicles been provided?
|  |  | EL-19 | For equipment/processes not on standby power, has UPS or other means been provided to move system to "safe" condition upon loss of power? This is particularly focused on valve and gate closure.
|  |  | EL-20 | Infrared, (IR) windows shall be installed in Motor Control Centers (MCC), low voltage switchgear, transformers, medium and high voltage switchgear, and other electrical equipment panel covers and/or doors. Design approach is to include a contract allowance for number of IR windows, with electrical gear supplier suggesting IR window placement.
INSTRUMENTATION & CONTROLS
|  |  | I&C-1 | Are all vendor control panels fully connected to SCADA system?
|  |  | I&C-2 | Do all PLC's have UPS sufficient to maintain operation until transfer to standby power is complete?
|  |  | I&C-3 | Are all PLC's provided with spare or space for 25% additional DI, DO, AI, AO?
|  |  | I&C-4 | Are control panels, PLC, HIM, housed in enclosures appropriate to the environment in which they are located?
|  |  | I&C-5 | Have products on which the Owner has standardized been used?
|  |  | I&C-6 | Have plant-wide communication networks been limited in number as much as possible and have Owner standard networks been used?
|  |  | I&C-7 | Is PLC programming to be provided by approved vendor?
|  |  | I&C-8 | Is there a 120 V convenience outlet provided at each PLC?
|  |  | I&C-9 | Do all PLC's have cabinet coolers or are they located in room which limits maximum temperature to 90 deg F?
BUILDINGS
|  |  | BDG-1 | Are doors large enough to get the largest piece of equipment in and out of the building? This may include removable astragal or transon panels.
|  |  | BDG-2 | Air Conditioning is sized to building loads including heat rejected from mechanical equipment and electrical gear.
|  |  | BDG-3 | Do buildings have a functional but not inconvenient security system?
|  |  | BDG-4 | What are building lighting controls? Switches? If, yes conveniently located? Motion sensed?
|  |  | BDG-5 | Are there appropriate windows from control/office areas into process areas?
|  |  | BDG-6 | Is there sufficient storage areas and types of areas? (E.g. spare parts, maintenance tools, shop tools, cleaning supplies, office supplies, plant records)
|  |  | BDG-7 | Have electronic door hardware and card readers been provided ?
|  |  | BDG-8 | Have door lock keying been incorporated into utility wide scheme?
|  |  | BDG-9 | Are bathroom and locker room facilities adequate in size and function?
|  |  | BDG-10 | Is the building ADA compliant
|  |  | BDG-11 | Do office, control room and lab areas have sufficient noise and vibration separation from process areas?
|  |  | BDG-12 | Have exterior windows been provided to allow sufficient natural daylight?
|  |  | BDG-13 | Are wall finishes sufficiently durable?
|  |  | BDG-14 | Are hallways wide enough?
|  |  | BDG-15 | Is there emergency lighting and is it sufficient?
|  |  | BDG-16 | Are interior and exterior doors conveniently located?
|  |  | BDG-17 | Are there canopies at exterior doors?
|  |  | BDG-18 | Is there space to hang-up wet gear and place boots?
|  |  | BDG-19 | Is there a janitors closet? Does it have adaquate storage space and a mop sink?
|  |  | BDG-20 | Are floor slabs designed for any vehicle wheel load planned for the space?
|  |  | BDG-21 | Are ceiling heights high enough for the building function?
|  |  | BDG-22 | Has space been provided for telephone and internet equipment?
|  |  | BDG-23 | Has need forfire suppression system been evaluated?
|  |  | BDG-24 | If fire suppression system is required has adaquate system been designed?
|  |  | BDG-25 | Are necessary safety equipment/alarms provided?
|  |  | BDG-26 | Is there an elevator to second and higher floors? Is it sized for equipment that needs to be moved?
CUSTOM
CUS-1
CUS-2
CUS-3
CUS-4
CUS-5
CUS-6
CUS-7
CUS-8
CUS-9
CUS-10
CUS-11